## Slide 1
Specifications | F51315
Capacity | 315Ah
Nominal Voltage | 51.2 Volts
Full Charge Resting Voltage | 56.0 Volts
Energy Storage | 16128Wh (16.128KWh)
Run time @ 100 Amp load | 4 Hours @ 77°F (25℃)
Self Discharge Rate | ≤4%/Month
Charging | 
Charging Temperate Range | 24~131°F
Charge Method | CC/CV
Absorb Voltage(CC) | 56.0 to 56.8 Volts
Maximum Current | 200Amps @ 77°F (25℃)
Recommended Current | 100Amps
Recommended CV Time | 15 minutes
Charge Efficiency | 99%
Discharging | 
Discharging Temperate Range | -4~140°F
Discharge Current | 200Amps Continuous
Discharge Current 3 seconds | 500Amps
Discharge Cut-off Voltage | 40Volts; Any cell (2.5 Volts)
Recommended Low Voltage Disconnect | 43.2 Volts
Short Circuit Protection | 3000A for 900µS
Short Circuit Protection Release | Disconnect the load
Battery Protection | 
EMS Control | PCM
Over Voltage, per Cell, Open | 3.65 Volts ± 0.03 Volts
Over Voltage, per Cell, Release | 3.50Volts ± 0.05 Volts
Over Discharge, per Cell, Open | 2.5 Volts ± 0.05 Volts
Over Discharge, per Cell, Release | 2.7 Volts ± 0.05 Volts
Over Current | 1000Amps 5mS
Over Current Release | Disconnect the charger or load
Over Temperature | 140°F (60℃)
Over Temperature Release | 122°F (50℃)
Low Temperature Charge, Open | 24°F
Low Temperature Charge, Release | 32°F
MOSFET Over Temperature, Open | 194°F
MOSFET Over Temperature, Release | 158°F
Mechanical | 
Length | 29.52’’（750mm）
Width | 12.99’’ (330mm)
Height | 25.59’’ (650mm)
Weight | 484 Pounds (220Kg)
Hardware | M8 Bolts, Washer, Lock Washer
Hardware Torque | 80 in - lb. (9 N-m)
Miscellaneous | 
Discharge Test | 100% DoD @ 1C
Discharge Test Results | ＞3000 cycles ~ 80% remaining Capactiy
Storage Method | 50% SoC, test @ 90 Days, recharge if below 43.2V
Storage Temperature Range(Recommended) | -4°F ~ 95°F (-20℃ - 35℃)
Lithium ion Chemistry | Lithium Iron Phosphate (LiFePo4)
Cell Type | Nano Prismatic
Internal Impedance(50% SoC) | ＜ 25mΩ